## Parameters
Woodward Program Parameters | Cells in blue are user inputs for calculations.
| Parameter | Generator #1 | Generator #2 | Comments
Generator Type | 235 | Synchronous | Synchronous
System Frequency [Hz] | 1750 | 60 | 60
Engine Speed [RPM] | 1601 | 1800 | 1800
Generator Rated Voltage [V] | 1766 | 480 | 13800 | Line to Line Voltage
Mains Rated Voltage [V] | 1768 | 480 | 13800 | Line to Line Voltage
Busbar 1 Rated Voltage [V] | 1781 | 277 | 7967 | Line to Line Voltage
Generator Rated Apparent Power [kVA] |  | 1075 | 4000 | Nameplate Ratings
Generator Power Factor |  | 0.85 | 0.85 | Nameplate Ratings
Generator Rated Active Power Calculation [kW] |  | 913.75 | 3400
Generator Rated Reactive Power Calculation [kVAR] |  | 566.2914 | 2107.1308
Generator Rated Active Power [kW] | 1752 | 900 | 3400
Generator Rated Reactive Power [kVAR] | 1758 | 625 | 2100
Generator Rated Current Calculation [A] |  | 1903.6458 | 246.3768
Generator Rated Current [A] | 1754 | 2500 | 300
Mains Rated Active Power [kW] | 1748 | 5000
Mains Rated Reactive Power [kVAR] | 1743 | 3500
Mains Rated Current | 1785 | 13900
1Ph2W Voltage Measuring | 1858 | Phase to Neutral | Phase to Neutral
1Ph2W Phase Rotation | 1859 | CW | CW
Generator Voltage Measuring | 1851 | 3Ph 4W | 3Ph 4W
Generator Current Measuring | 1850 | L1 L2 L3 | L1 L2 L3
Mains Voltage Measuring | 1853 | 3Ph 4W | 3Ph 4W
Mains Current Input | 1854 | Mains Current | Mains Current
Mains Current Measuring | 1852 | Phase L1 | Phase L1
System Rated Active Power [kW] | 1825 | 900 | 4000
Generator PT Primary Rated Voltage [V] | 1801 | 277 | 7967 | Line to Nuetral Voltage
Generator PT Secondary Rated Voltage [V] | 1800 | 120 | 120 | Line to Nuetral Voltage
Generator CT Primary Rated Current [A/x] | 1806 | 10000 | 10000
Ground CT Primary Rated Current [A/x] | 1810 | 500 | 500
Busbar 1 PT Primary Rated Voltage [V] | 1813 | 277 | 7967 | Line to Nuetral Voltage
Busbar 1 PT Secondary Rated Voltage [V] | 1812 | 120 | 120 | Line to Nuetral Voltage
Mains PT Primary Rated Voltage [V] | 1804 | 277 | 7967 | Line to Nuetral Voltage
Mains PT Secondary Rated Voltage | 1803 | 120 | 120 | Line to Nuetral Voltage
Mains CT Primary Rated Current [A/x] | 1807 | 10000 | 10000