## Physical IO
# | Function | Type | Configured For | Terminal | TRUE | HIL DO | HIL DI |  |  | Configure settings | 60kW TQG Setup | Configured For
| Common | Digital Input | n/a | 66 | Ground | 20 |  |  |  | Check logic operation of the relays | Common
1 | Emergency Stop | Digital Input | Alarm | 67 | NC | 1 |  | HIL Used | 1 | Wire and power the HIL DI | E-stop | Control
2 | Start in Auto | Digital Input | Control | 68 |  | 2 |  | HIL Used | 2 | Logic for HIL DI | Run Mode | Control
3 | Low Oil Pressure | Digital Input | Alarm | 69 | [5 empty] | Configuration file of the 60kW for 900kW and compare and contrast | Auxiliary Fuel | Control
4 | Coolant Temp. | Digital Input | Alarm | 70 | [6 empty] | Not used
5 | External alarm acknowledge | Digital Input | Control | 71 |  | 3 |  | HIL Used | 3 |  | AC Breaker Close | Control
6 | Enable MCB | Digital Input | Control | 72 |  | 4 |  | HIL Used | 4 |  | AC Breaker Open | Control
7 | Reply MCB is open | Digital Input | Control | 73 |  | 5 |  | HIL Used | 5 |  | MCB Open | Feedback
8 | Reply GCB is open | Digital Input | Control | 74 |  | 6 |  | HIL Used | 6 |  | GCB Open | Feedback
9 | Discrete input configurable | [9 empty] | Engine Start | Control
10 | Spare | [9 empty] | Not used
11 | MCB | Orange | Grey | 77 |  | 9 |  | HIL Used | 7 |  | Battle Short | Control
12 | GCB | Yellow | Purple | 78 |  | 10 |  | HIL Used | 8 |  | Not used
1 | Ready for operation | Digital Output | n/a | 41 |  |  | 1 | ?
| Power | Digital Output | n/a | 42 | Up to 250 Vac/Vdc (15V) |  | 0
2 | Centralized Alarm (Horn) | Digital Output | n/a | 43 |  |  | 2
3 | Starter (Crank) | Digital Output | n/a | 44 |  |  | 3 | HIL Used | 1
4 | Fuel Solenoid (Fuel Valve) | Digital Output | n/a | 45 |  |  | 4 | HIL Used | 2
| Power | Digital Output | n/a | 46 |  |  | 0
5 | Preglow | Digital Output | n/a | 47 |  |  | 5
| Power | Digital Output | n/a | 48 |  |  | 0
6 | Close GCB | Digital Output | n/a | 49 |  |  | 6 | HIL Used | 3
| Power | Digital Output | n/a | 50 |  |  | 0
7 | Open GCB | Digital Output | n/a | 51 |  |  | 7 | HIL Used | 4
| Power | Digital Output | n/a | 52 |  |  | 0
8 | Close MCB | Digital Output | n/a | 53 |  |  | 8 | HIL Used | 5
| Power | Digital Output | n/a | 54 |  |  | 0
9 | Open MCB | Digital Output | n/a | 55 |  |  | 9 | HIL Used | 6
| Power | Digital Output | n/a | 56 |  |  | 0
10 | Auxillary Services (Lube Pump) | Digital Output | n/a | 57 |  |  | 10
11 | Alarm Class A or B (Warning Signal) | Digital Output | n/a | 58 |  |  | 11 | Spare | 7
12 | Alarm Class C-F (Shutdown Signal) | Digital Output | n/a | 59 |  |  | 12 | Spare | 8
| Power | Digital Output | n/a | 60 |  |  | 0
1 | Fuel Level | Analog Input
2 | Engine Coolant Temperature | Analog Input
3 | Engine Oil Pressure | Analog Input
Modbus
| Generator Start and Stop |  | RC Bit 1
| Close and Open AC Output Contactor |  | RC Bit 2
| Frequency Droop On and Off |  | RC Bit 3
| Auxialiary Fuel Function On and Off |  | RC Bit 4
| Disable Voltage Droop |  | RC Bit 16
| Set Generator Output Frequency |  | Frequency Set Point (Par. 4762)
| Set Generator Output Voltage |  | Voltage Set Point (Par. 4763)

## LM Flag
Logics Manager Flags
# | Function |  | Type
1 | (Gen Start and not RC Bit 1) and 1 | Remote Engine Start | 60 kW TQG
2 | (LM1 or LM2) and LM7 |  | 60 kW TQG
3 |  |  | 60 kW TQG
4 |  |  | 60 kW TQG
5 |  |  | 60 kW TQG
6 |  |  | 60 kW TQG
7 |  |  | 60 kW TQG
8 |  |  | 60 kW TQG
9 |  |  | 60 kW TQG
10 |  |  | 60 kW TQG
11
12
13
14
15
16